CLENDENIN VOLUNTEER FIRE DEPARTMENT

STANDARD OPERATING GUIDLINE

Subject: Knox Rapid Entry System

Policy:

Clendenin Volunteer Fire Department has adopted the Knox Rapid Entry System (KRES) as its standard system for fire department key boxes. KRES products may be required to protect fire department connections or provide fire

department access and control of electric gate openers.

Key Boxes: When required

Fire department key boxes shall be required whenever:

- A building has a fire alarm system or fire sprinkler system.

- A building has an elevator

- A commercial business that use, store, manufacture or process on site hazardous materials that must be reported under Title III of the Federal Super Fund Amendments

- A commercial business, Restaurant, Church, and healthcare facility

- Apartment buildings

- A building has unreasonable delays for fire department access as determined by the Fire Chief or his/her designee

Key Boxes: Size, Location, and Installation

The provisions of this section are a minimum requirement that may be superseded during the

comprehensive planning process. In some cases, the Fire Chief or his/her designee may accept

performance-based alternatives or require a greater level of building access for lifesaving or

firefighting purposes.

The size of the required key box is dependent on building size and/or configuration:

Less than seven stories, less than 50,000 sq ft: Knox 3200 Series

Less than seven stories, greater than 50,000 sq ft: Knox 4400 Series

All key boxes shall be of the hinged type; “lift-off” lids are not permitted.

Key boxes shall be located at the main entrance to the building or other location approved by the

Fire Chief or his/her designee. Key boxes are preferred to be at a height of six (6) feet above

finished grade, but must be no lower than five (5) feet or no higher than six (6) feet above

finished grade. All measurements shall be to the centerline of the box.

Key Boxes: Contents

Each key set must include:

Keys to provide access to all portions of the building

One (1) electrical panel key

If the building is equipped with a fire alarm system: One (1) fire alarm key

If the building is equipped with an elevator: One (1) elevator key

The following number of key sets shall be required based on the building size and/or

configuration:

Single story, less than 50,000 sq ft: One set

Single story, greater than 50,000 sq ft: Three sets

Two to six stories, less than 50,000 sq ft: Two sets

Two to six stories, greater than 50,000 sq ft: Three sets

The Fire chief or his/her designee may require a different number of key sets dependent on

the building size, configuration, or to provide a greater level of building access for lifesaving or

firefighting purposes.

Fire Apparatus Access Roads: Gate Controls

This section shall be applicable to access control systems for security gates

Where a security gate is installed in such a manner to obstruct a required Fire Apparatus Access

Road, the gate must be provided with hardware that is compatible with the department KRES. If the gate is a manually operated gate, the gate must be equipped with a Knox 3781, 3782, 3783 or 3784 series padlock. If the gate is automatically operated via an electrical or mechanical opener, the gate must be equipped with a Knox 3502 or 3503 series electrical key switch that is configured to override the gate controller and hold the gate open for fire department access.